## Notes & Instructions
PLEASE NOTE THE FOLLOWING:
- Values given in this Loop Load Calculator must only be used as a guide as site conditions may influence results.
- Installers must perform their own tests of the system to confirm successful operation of the system.
- This model assumes that the installation is SANS 10139 compliant.
INSTRUCTIONS:
1) The sheet is protected. Data can only be entered into the Green fields
2) Enter project details in the Project Header fields.
3) Complete the calculation for one loop at a time.
4) Populate the table with all the devices on the loop.
5) The sheet will indicate the maximum permissible cable Length for both 1mm² and 1.5mm² cable.
6) The sheet will also indicate the expected maximum Loop Resistance which must be checked against actual loop resistance as measured with a multi-meter.
7) The sheet will also indicate if the loop loading in quiescent and alarm condition is compliant.
See example below:
In this example, the maximum cable return length for 1mm² cable is 950m and 1,350m for 1.5mm².
The maximum expected loop resistance is 14.86 and 14.90 Ohms respectively.

## Loop Load Calculator 1
Project:
Loop:
Loop Description:
GREEN CELLS BELOW INDICATE MAXIMUM PERMISSABLE LOOP LENGTH
Part number | Description | Current Draw Quiescent | Current Draw Alarm | Quantity | Current Total Alarm | Current Total Quiesent | Loop Length 1mm multicore | Loop Resistance ohm | Loop Length 1.5mm multicore | Loop Resistance ohm | Char Wire | Char Wire + Conatct | Char Wire | Char Wire + Contact | Detector per section | Current draw AVE | Current per sec | Volt Drop | Volt Drop X 12 | Volt Drop | Volt Drop X 12
PANELS | [6 empty] | 150 | 2.15 | 150 | 1.5176 | 1.77 | 2.15 | 1.3275 | 1.5176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GEKKO | GEKKO Addressable 2.4 Amp PSU | 65 | 65 |  | 0 | 0 | 200 | 2.8667 | 200 | 2.0235 | 2.36 | 2.8667 | 1.77 | 2.0235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON MINI REPEATER -NETWORKED | GEKKO Mini Repeater for Networks | 65 | 65 |  | 0 | 0 | 250 | 3.5833 | 250 | 2.5294 | 2.95 | 3.5833 | 2.2125 | 2.5294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON DISPLAY REPEATER -SINGLE USE | GEKKO Single use Repeater | 65 | 65 |  | 0 | 0 | 300 | 4.3 | 300 | 3.0353 | 3.54 | 4.3 | 2.655 | 3.0353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
OCTO+ - 1 LOOP | OCTO+ Addressable Panel 1 Loop 2.4 Amp PSU | 80 | 80 |  | 0 | 0 | 350 | 5.0167 | 350 | 3.5412 | 4.13 | 5.0167 | 3.0975 | 3.5412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
528-E | NODE PLUS | 80 | 80 |  | 0 | 0 | 400 | 5.7333 | 400 | 4.0471 | 4.72 | 5.7333 | 3.54 | 4.0471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
DETECTORS | [6 empty] | 450 | 6.45 | 450 | 4.5529 | 5.31 | 6.45 | 3.9825 | 4.5529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830 | Addressable Multisensor - EN54 Certified | 0.55 |  |  | 0 | 0 | 500 | 7.1667 | 500 | 5.0588 | 5.9 | 7.1667 | 4.425 | 5.0588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830CO | Addressable Multisensor with CO & Pre-Alarm function | 0.65 |  |  | 0 | 0 | 550 | 7.8833 | 550 | 5.5647 | 6.49 | 7.8833 | 4.8675 | 5.5647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA831 | Addressable Multisensor with Sounder Beacon - EN54 Certified | 0.55 | 8.9 |  | 0 | 0 | 600 | 8.6 | 600 | 6.0706 | 7.08 | 8.6 | 5.31 | 6.0706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
REMOTE INDICATORS | [6 empty] | 650 | 9.3167 | 650 | 6.5765 | 7.67 | 9.3167 | 5.7525 | 6.5765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-C | Conventional Minidisc Remote Indicator |  | 2 |  | 0 | 0 | 700 | 10.0333 | 700 | 7.0824 | 8.26 | 10.0333 | 6.195 | 7.0824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-A | Addressable Remote Indicator | 0.3 | 7 |  | 0 | 0 | 750 | 10.75 | 750 | 7.5882 | 8.85 | 10.75 | 6.6375 | 7.5882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LINE MODULES | [6 empty] | 800 | 11.4667 | 800 | 8.0941 | 9.44 | 11.4667 | 7.08 | 8.0941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAM | Addressable Manually Addressed Module | 1.8 | 12 |  | 0 | 0 | 850 | 12.1833 | 850 | 8.6 | 10.03 | 12.1833 | 7.5225 | 8.6 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O | Addressable I/O Module with Isolator & Dual Gang Box | 1.3 | 2.9 |  | 0 | 0 | 900 | 12.9 | 900 | 9.1059 | 10.62 | 12.9 | 7.965 | 9.1059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-AD-ISO | Addressable Stand Alone Loop Isolator | 1 | 1.65 |  | 0 | 0 | 950 | 13.6167 | 950 | 9.6118 | 11.21 | 13.6167 | 8.4075 | 9.6118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O-ISO | Addressable INPUT / OUTPUT Module | 0.5 | 2 |  | 0 | 0 | 1000 | 14.3333 | 1000 | 10.1176 | 11.8 | 14.3333 | 8.85 | 10.1176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAINS I/O | Addressable Mains Switching INPUT / OUTPUT Module | 1.3 | 2.9 |  | 0 | 0 | 1050 | 15.05 | 1050 | 10.6235 | 12.39 | 15.05 | 9.2925 | 10.6235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
INPUT | Addressable INPUT MODULE | 0.5 | 2 |  | 0 | 0 | 1100 | 15.7667 | 1100 | 11.1294 | 12.98 | 15.7667 | 9.735 | 11.1294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LSCISO | Addressable Opto Isolated Loop Sounder Controller (Ext Power) | 0 | 0 |  | 0 | 0 | 1150 | 16.4833 | 1150 | 11.6353 | 13.57 | 16.4833 | 10.1775 | 11.6353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZMU | Addressable Zone Monitoring Unit | 1.8 | 25 |  | 0 | 0 | 1200 | 17.2 | 1200 | 12.1412 | 14.16 | 17.2 | 10.62 | 12.1412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
QUAD ZMU | Addressable Conventional Zone Monitoring Unit | 1.8 |  |  | 0 | 0 | 1250 | 17.9167 | 1250 | 12.6471 | 14.75 | 17.9167 | 11.0625 | 12.6471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 INPUT | Addressable 4 Input | 2.6 |  |  | 0 | 0 | 1300 | 18.6333 | 1300 | 13.1529 | 15.34 | 18.6333 | 11.505 | 13.1529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 INPUT | Addressable 8 Input | 3.2 |  |  | 0 | 0 | 1350 | 19.35 | 1350 | 13.6588 | 15.93 | 19.35 | 11.9475 | 13.6588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CCPI 8 ZONES | Addressable Conventional Control Panel Interface Up To 8 Zones | 3.2 |  |  | 0 | 0 | 1400 | 20.0667 | 1400 | 14.1647 | 16.52 | 20.0667 | 12.39 | 14.1647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
SPRINKLER SWITCH | Addressable Sprinkler Switch Module | 0.55 |  |  | 0 | 0 | 1450 | 20.7833 | 1450 | 14.6706 | 17.11 | 20.7833 | 12.8325 | 14.6706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CALL POINTS | [6 empty] | 1500 | 21.5 | 1500 | 15.1765 | 17.7 | 21.5 | 13.275 | 15.1765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-A | Addressable Call Point Red Resettable IP24 | 0.45 |  |  | 0 | 0 | 1550 | 22.2167 | 1550 | 15.6824 | 18.29 | 22.2167 | 13.7175 | 15.6824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-AI | Addressable Call Point Red Resettable IP24 with Loop Isolator | 0.65 |  |  | 0 | 0 | 1600 | 22.9333 | 1600 | 16.1882 | 18.88 | 22.9333 | 14.16 | 16.1882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
STANDALONE SOUNDER/BEACONS | [6 empty] | 1650 | 23.65 | 1650 | 16.6941 | 19.47 | 23.65 | 14.6025 | 16.6941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AS | Addressable VALKYRIE AS Sounder IP21 (RED) | 0.5 | 7.5 |  | 0 | 0 | 1700 | 24.3667 | 1700 | 17.2 | 20.06 | 24.3667 | 15.045 | 17.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AB | Addressable VALKYRIE AB Beacon IP21 (RED) | 0.5 | 1.4 |  | 0 | 0 | 1750 | 25.0833 | 1750 | 17.7059 | 20.65 | 25.0833 | 15.4875 | 17.7059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASB | Addressable VALKYRIE ASB Sounder Beacon IP21 (RED) | 0.5 | 8.9 |  | 0 | 0 | 1800 | 25.8 | 1800 | 18.2118 | 21.24 | 25.8 | 15.93 | 18.2118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASI | Addressable VALKYRIE ASI Sounder IP21 with Isolator (RED) | 0.65 | 7.65 |  | 0 | 0
VALKYRIE ABI | Addressable VALKYRIE ABI Beacon IP21 with Isolator (RED) | 0.65 | 1.55 |  | 0 | 0
VALKYRIE ASBI | Addressable VALKYRIE ASBI Sounder Beacon IP21 with Isolator | 0.65 | 9.05 |  | 0 | 0
VULCAN 2 AS | Addressable Vulcan AS Sounder IP21 (RED) | 0.5 | 7 |  | 0 | 0
VULCAN 2 AB | Addressable Vulcan AB Beacon IP21 (RED) | 0.5 | 2.5 |  | 0 | 0
VULCAN 2 ASB | Addressable Vulcan ASB Sounder Beacon IP21 (RED) | 0.5 | 8 |  | 0 | 0
VOICE SOUNDERS
GFE P.A. VOX -A | Addressable P.A. Speaker Amplifier Dual Gang Box | 0.5 | 0.5 |  | 0 | 0
VALKYRIE VOX - A | VALKYRIE Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VALKYRIE VOX - AB | VALKYRIE Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
VULCAN 2 VOX - A | VULCAN Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VULCAN 2 VOX - AB | VULCAN Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
DOOR HOLDERS
GFE-DHA-ISOLATOR | Addressable Magnetic Door Holder (200N) - ULOW POWER | 0.8 | 7 |  | 0 | 0
LOOP POWERED BEAMS
FIREBEAM BLUE | Firebeam Blue - distance of 7 - 70 meters (Maximum of 6 per Loop) | 24 | 24 |  | 0 | 0
| Loop total devices (excl panels & repeaters) | 0 | LOOP GOOD
| Total quiesent current draw mA (Max 150mA) | 0 | [8 empty] | 1
| Total alarm current draw mA (Max 900mA) | 0 | [8 empty] | 1
| Contact resistance | 0
| Loop total dveices | 0 |  | 0 | 0
Total quiesent current draw
| Total alarm current draw mA | 0 | 0
| Contact reistance | 0.04

## Loop Load Calculator 2
Project:
Loop:
Loop Description:
GREEN CELLS BELOW INDICATE MAXIMUM PERMISSABLE LOOP LENGTH
Part number | Description | Current Draw Quiescent | Current Draw Alarm | Quantity | Current Total Alarm | Current Total Quiesent | Loop Length 1mm multicore | Loop Resistance ohm | Loop Length 1.5mm multicore | Loop Resistance ohm | Char Wire | Char Wire + Conatct | Char Wire | Char Wire + Contact | Detector per section | Current draw AVE | Current per sec | Volt Drop | Volt Drop X 12 | Volt Drop | Volt Drop X 12
PANELS | [6 empty] | 150 | 2.15 | 150 | 1.5176 | 1.77 | 2.15 | 1.3275 | 1.5176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GEKKO | GEKKO Addressable 2.4 Amp PSU | 65 | 65 |  | 0 | 0 | 200 | 2.8667 | 200 | 2.0235 | 2.36 | 2.8667 | 1.77 | 2.0235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON MINI REPEATER -NETWORKED | GEKKO Mini Repeater for Networks | 65 | 65 |  | 0 | 0 | 250 | 3.5833 | 250 | 2.5294 | 2.95 | 3.5833 | 2.2125 | 2.5294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON DISPLAY REPEATER -SINGLE USE | GEKKO Single use Repeater | 65 | 65 |  | 0 | 0 | 300 | 4.3 | 300 | 3.0353 | 3.54 | 4.3 | 2.655 | 3.0353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
OCTO+ - 1 LOOP | OCTO+ Addressable Panel 1 Loop 2.4 Amp PSU | 80 | 80 |  | 0 | 0 | 350 | 5.0167 | 350 | 3.5412 | 4.13 | 5.0167 | 3.0975 | 3.5412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
528-E | NODE PLUS | 80 | 80 |  | 0 | 0 | 400 | 5.7333 | 400 | 4.0471 | 4.72 | 5.7333 | 3.54 | 4.0471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
DETECTORS | [6 empty] | 450 | 6.45 | 450 | 4.5529 | 5.31 | 6.45 | 3.9825 | 4.5529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830 | Addressable Multisensor - EN54 Certified | 0.55 |  |  | 0 | 0 | 500 | 7.1667 | 500 | 5.0588 | 5.9 | 7.1667 | 4.425 | 5.0588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830CO | Addressable Multisensor with CO & Pre-Alarm function | 0.65 |  |  | 0 | 0 | 550 | 7.8833 | 550 | 5.5647 | 6.49 | 7.8833 | 4.8675 | 5.5647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA831 | Addressable Multisensor with Sounder Beacon - EN54 Certified | 0.55 | 8.9 |  | 0 | 0 | 600 | 8.6 | 600 | 6.0706 | 7.08 | 8.6 | 5.31 | 6.0706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
REMOTE INDICATORS | [6 empty] | 650 | 9.3167 | 650 | 6.5765 | 7.67 | 9.3167 | 5.7525 | 6.5765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-C | Conventional Minidisc Remote Indicator |  | 2 |  | 0 | 0 | 700 | 10.0333 | 700 | 7.0824 | 8.26 | 10.0333 | 6.195 | 7.0824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-A | Addressable Remote Indicator | 0.3 | 7 |  | 0 | 0 | 750 | 10.75 | 750 | 7.5882 | 8.85 | 10.75 | 6.6375 | 7.5882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LINE MODULES | [6 empty] | 800 | 11.4667 | 800 | 8.0941 | 9.44 | 11.4667 | 7.08 | 8.0941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAM | Addressable Manually Addressed Module | 1.8 | 12 |  | 0 | 0 | 850 | 12.1833 | 850 | 8.6 | 10.03 | 12.1833 | 7.5225 | 8.6 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O | Addressable I/O Module with Isolator & Dual Gang Box | 1.3 | 2.9 |  | 0 | 0 | 900 | 12.9 | 900 | 9.1059 | 10.62 | 12.9 | 7.965 | 9.1059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-AD-ISO | Addressable Stand Alone Loop Isolator | 1 | 1.65 |  | 0 | 0 | 950 | 13.6167 | 950 | 9.6118 | 11.21 | 13.6167 | 8.4075 | 9.6118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O-ISO | Addressable INPUT / OUTPUT Module | 0.5 | 2 |  | 0 | 0 | 1000 | 14.3333 | 1000 | 10.1176 | 11.8 | 14.3333 | 8.85 | 10.1176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAINS I/O | Addressable Mains Switching INPUT / OUTPUT Module | 1.3 | 2.9 |  | 0 | 0 | 1050 | 15.05 | 1050 | 10.6235 | 12.39 | 15.05 | 9.2925 | 10.6235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
INPUT | Addressable INPUT MODULE | 0.5 | 2 |  | 0 | 0 | 1100 | 15.7667 | 1100 | 11.1294 | 12.98 | 15.7667 | 9.735 | 11.1294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LSCISO | Addressable Opto Isolated Loop Sounder Controller (Ext Power) | 0 | 0 |  | 0 | 0 | 1150 | 16.4833 | 1150 | 11.6353 | 13.57 | 16.4833 | 10.1775 | 11.6353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZMU | Addressable Zone Monitoring Unit | 1.8 | 25 |  | 0 | 0 | 1200 | 17.2 | 1200 | 12.1412 | 14.16 | 17.2 | 10.62 | 12.1412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
QUAD ZMU | Addressable Conventional Zone Monitoring Unit | 1.8 |  |  | 0 | 0 | 1250 | 17.9167 | 1250 | 12.6471 | 14.75 | 17.9167 | 11.0625 | 12.6471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 INPUT | Addressable 4 Input | 2.6 |  |  | 0 | 0 | 1300 | 18.6333 | 1300 | 13.1529 | 15.34 | 18.6333 | 11.505 | 13.1529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 INPUT | Addressable 8 Input | 3.2 |  |  | 0 | 0 | 1350 | 19.35 | 1350 | 13.6588 | 15.93 | 19.35 | 11.9475 | 13.6588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CCPI 8 ZONES | Addressable Conventional Control Panel Interface Up To 8 Zones | 3.2 |  |  | 0 | 0 | 1400 | 20.0667 | 1400 | 14.1647 | 16.52 | 20.0667 | 12.39 | 14.1647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
SPRINKLER SWITCH | Addressable Sprinkler Switch Module | 0.55 |  |  | 0 | 0 | 1450 | 20.7833 | 1450 | 14.6706 | 17.11 | 20.7833 | 12.8325 | 14.6706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CALL POINTS | [6 empty] | 1500 | 21.5 | 1500 | 15.1765 | 17.7 | 21.5 | 13.275 | 15.1765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-A | Addressable Call Point Red Resettable IP24 | 0.45 |  |  | 0 | 0 | 1550 | 22.2167 | 1550 | 15.6824 | 18.29 | 22.2167 | 13.7175 | 15.6824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-AI | Addressable Call Point Red Resettable IP24 with Loop Isolator | 0.65 |  |  | 0 | 0 | 1600 | 22.9333 | 1600 | 16.1882 | 18.88 | 22.9333 | 14.16 | 16.1882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
STANDALONE SOUNDER/BEACONS | [6 empty] | 1650 | 23.65 | 1650 | 16.6941 | 19.47 | 23.65 | 14.6025 | 16.6941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AS | Addressable VALKYRIE AS Sounder IP21 (RED) | 0.5 | 7.5 |  | 0 | 0 | 1700 | 24.3667 | 1700 | 17.2 | 20.06 | 24.3667 | 15.045 | 17.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AB | Addressable VALKYRIE AB Beacon IP21 (RED) | 0.5 | 1.4 |  | 0 | 0 | 1750 | 25.0833 | 1750 | 17.7059 | 20.65 | 25.0833 | 15.4875 | 17.7059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASB | Addressable VALKYRIE ASB Sounder Beacon IP21 (RED) | 0.5 | 8.9 |  | 0 | 0 | 1800 | 25.8 | 1800 | 18.2118 | 21.24 | 25.8 | 15.93 | 18.2118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASI | Addressable VALKYRIE ASI Sounder IP21 with Isolator (RED) | 0.65 | 7.65 |  | 0 | 0
VALKYRIE ABI | Addressable VALKYRIE ABI Beacon IP21 with Isolator (RED) | 0.65 | 1.55 |  | 0 | 0
VALKYRIE ASBI | Addressable VALKYRIE ASBI Sounder Beacon IP21 with Isolator | 0.65 | 9.05 |  | 0 | 0
VULCAN 2 AS | Addressable Vulcan AS Sounder IP21 (RED) | 0.5 | 7 |  | 0 | 0
VULCAN 2 AB | Addressable Vulcan AB Beacon IP21 (RED) | 0.5 | 2.5 |  | 0 | 0
VULCAN 2 ASB | Addressable Vulcan ASB Sounder Beacon IP21 (RED) | 0.5 | 8 |  | 0 | 0
VOICE SOUNDERS
GFE P.A. VOX -A | Addressable P.A. Speaker Amplifier Dual Gang Box | 0.5 | 0.5 |  | 0 | 0
VALKYRIE VOX - A | VALKYRIE Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VALKYRIE VOX - AB | VALKYRIE Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
VULCAN 2 VOX - A | VULCAN Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VULCAN 2 VOX - AB | VULCAN Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
DOOR HOLDERS
GFE-DHA-ISOLATOR | Addressable Magnetic Door Holder (200N) - ULOW POWER | 0.8 | 7 |  | 0 | 0
LOOP POWERED BEAMS
FIREBEAM BLUE | Firebeam Blue - distance of 7 - 70 meters (Maximum of 6 per Loop) | 24 | 24 |  | 0 | 0
| Loop total devices (excl panels & repeaters) | 0 | LOOP GOOD
| Total quiesent current draw mA (Max 150mA) | 0 | [8 empty] | 1
| Total alarm current draw mA (Max 900mA) | 0 | [8 empty] | 1
| Contact resistance | 0
| Loop total dveices | 0 |  | 0 | 0
Total quiesent current draw
| Total alarm current draw mA | 0 | 0
| Contact reistance | 0.04

## Loop Load Calculator 3
Project:
Loop:
Loop Description:
GREEN CELLS BELOW INDICATE MAXIMUM PERMISSABLE LOOP LENGTH
Part number | Description | Current Draw Quiescent | Current Draw Alarm | Quantity | Current Total Alarm | Current Total Quiesent | Loop Length 1mm multicore | Loop Resistance ohm | Loop Length 1.5mm multicore | Loop Resistance ohm | Char Wire | Char Wire + Conatct | Char Wire | Char Wire + Contact | Detector per section | Current draw AVE | Current per sec | Volt Drop | Volt Drop X 12 | Volt Drop | Volt Drop X 12
PANELS | [6 empty] | 150 | 2.15 | 150 | 1.5176 | 1.77 | 2.15 | 1.3275 | 1.5176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GEKKO | GEKKO Addressable 2.4 Amp PSU | 65 | 65 |  | 0 | 0 | 200 | 2.8667 | 200 | 2.0235 | 2.36 | 2.8667 | 1.77 | 2.0235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON MINI REPEATER -NETWORKED | GEKKO Mini Repeater for Networks | 65 | 65 |  | 0 | 0 | 250 | 3.5833 | 250 | 2.5294 | 2.95 | 3.5833 | 2.2125 | 2.5294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON DISPLAY REPEATER -SINGLE USE | GEKKO Single use Repeater | 65 | 65 |  | 0 | 0 | 300 | 4.3 | 300 | 3.0353 | 3.54 | 4.3 | 2.655 | 3.0353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
OCTO+ - 1 LOOP | OCTO+ Addressable Panel 1 Loop 2.4 Amp PSU | 80 | 80 |  | 0 | 0 | 350 | 5.0167 | 350 | 3.5412 | 4.13 | 5.0167 | 3.0975 | 3.5412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
528-E | NODE PLUS | 80 | 80 |  | 0 | 0 | 400 | 5.7333 | 400 | 4.0471 | 4.72 | 5.7333 | 3.54 | 4.0471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
DETECTORS | [6 empty] | 450 | 6.45 | 450 | 4.5529 | 5.31 | 6.45 | 3.9825 | 4.5529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830 | Addressable Multisensor - EN54 Certified | 0.55 |  |  | 0 | 0 | 500 | 7.1667 | 500 | 5.0588 | 5.9 | 7.1667 | 4.425 | 5.0588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830CO | Addressable Multisensor with CO & Pre-Alarm function | 0.65 |  |  | 0 | 0 | 550 | 7.8833 | 550 | 5.5647 | 6.49 | 7.8833 | 4.8675 | 5.5647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA831 | Addressable Multisensor with Sounder Beacon - EN54 Certified | 0.55 | 8.9 |  | 0 | 0 | 600 | 8.6 | 600 | 6.0706 | 7.08 | 8.6 | 5.31 | 6.0706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
REMOTE INDICATORS | [6 empty] | 650 | 9.3167 | 650 | 6.5765 | 7.67 | 9.3167 | 5.7525 | 6.5765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-C | Conventional Minidisc Remote Indicator |  | 2 |  | 0 | 0 | 700 | 10.0333 | 700 | 7.0824 | 8.26 | 10.0333 | 6.195 | 7.0824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-A | Addressable Remote Indicator | 0.3 | 7 |  | 0 | 0 | 750 | 10.75 | 750 | 7.5882 | 8.85 | 10.75 | 6.6375 | 7.5882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LINE MODULES | [6 empty] | 800 | 11.4667 | 800 | 8.0941 | 9.44 | 11.4667 | 7.08 | 8.0941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAM | Addressable Manually Addressed Module | 1.8 | 12 |  | 0 | 0 | 850 | 12.1833 | 850 | 8.6 | 10.03 | 12.1833 | 7.5225 | 8.6 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O | Addressable I/O Module with Isolator & Dual Gang Box | 1.3 | 2.9 |  | 0 | 0 | 900 | 12.9 | 900 | 9.1059 | 10.62 | 12.9 | 7.965 | 9.1059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-AD-ISO | Addressable Stand Alone Loop Isolator | 1 | 1.65 |  | 0 | 0 | 950 | 13.6167 | 950 | 9.6118 | 11.21 | 13.6167 | 8.4075 | 9.6118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O-ISO | Addressable INPUT / OUTPUT Module | 0.5 | 2 |  | 0 | 0 | 1000 | 14.3333 | 1000 | 10.1176 | 11.8 | 14.3333 | 8.85 | 10.1176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAINS I/O | Addressable Mains Switching INPUT / OUTPUT Module | 1.3 | 2.9 |  | 0 | 0 | 1050 | 15.05 | 1050 | 10.6235 | 12.39 | 15.05 | 9.2925 | 10.6235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
INPUT | Addressable INPUT MODULE | 0.5 | 2 |  | 0 | 0 | 1100 | 15.7667 | 1100 | 11.1294 | 12.98 | 15.7667 | 9.735 | 11.1294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LSCISO | Addressable Opto Isolated Loop Sounder Controller (Ext Power) | 0 | 0 |  | 0 | 0 | 1150 | 16.4833 | 1150 | 11.6353 | 13.57 | 16.4833 | 10.1775 | 11.6353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZMU | Addressable Zone Monitoring Unit | 1.8 | 25 |  | 0 | 0 | 1200 | 17.2 | 1200 | 12.1412 | 14.16 | 17.2 | 10.62 | 12.1412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
QUAD ZMU | Addressable Conventional Zone Monitoring Unit | 1.8 |  |  | 0 | 0 | 1250 | 17.9167 | 1250 | 12.6471 | 14.75 | 17.9167 | 11.0625 | 12.6471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 INPUT | Addressable 4 Input | 2.6 |  |  | 0 | 0 | 1300 | 18.6333 | 1300 | 13.1529 | 15.34 | 18.6333 | 11.505 | 13.1529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 INPUT | Addressable 8 Input | 3.2 |  |  | 0 | 0 | 1350 | 19.35 | 1350 | 13.6588 | 15.93 | 19.35 | 11.9475 | 13.6588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CCPI 8 ZONES | Addressable Conventional Control Panel Interface Up To 8 Zones | 3.2 |  |  | 0 | 0 | 1400 | 20.0667 | 1400 | 14.1647 | 16.52 | 20.0667 | 12.39 | 14.1647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
SPRINKLER SWITCH | Addressable Sprinkler Switch Module | 0.55 |  |  | 0 | 0 | 1450 | 20.7833 | 1450 | 14.6706 | 17.11 | 20.7833 | 12.8325 | 14.6706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CALL POINTS | [6 empty] | 1500 | 21.5 | 1500 | 15.1765 | 17.7 | 21.5 | 13.275 | 15.1765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-A | Addressable Call Point Red Resettable IP24 | 0.45 |  |  | 0 | 0 | 1550 | 22.2167 | 1550 | 15.6824 | 18.29 | 22.2167 | 13.7175 | 15.6824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-AI | Addressable Call Point Red Resettable IP24 with Loop Isolator | 0.65 |  |  | 0 | 0 | 1600 | 22.9333 | 1600 | 16.1882 | 18.88 | 22.9333 | 14.16 | 16.1882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
STANDALONE SOUNDER/BEACONS | [6 empty] | 1650 | 23.65 | 1650 | 16.6941 | 19.47 | 23.65 | 14.6025 | 16.6941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AS | Addressable VALKYRIE AS Sounder IP21 (RED) | 0.5 | 7.5 |  | 0 | 0 | 1700 | 24.3667 | 1700 | 17.2 | 20.06 | 24.3667 | 15.045 | 17.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AB | Addressable VALKYRIE AB Beacon IP21 (RED) | 0.5 | 1.4 |  | 0 | 0 | 1750 | 25.0833 | 1750 | 17.7059 | 20.65 | 25.0833 | 15.4875 | 17.7059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASB | Addressable VALKYRIE ASB Sounder Beacon IP21 (RED) | 0.5 | 8.9 |  | 0 | 0 | 1800 | 25.8 | 1800 | 18.2118 | 21.24 | 25.8 | 15.93 | 18.2118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASI | Addressable VALKYRIE ASI Sounder IP21 with Isolator (RED) | 0.65 | 7.65 |  | 0 | 0
VALKYRIE ABI | Addressable VALKYRIE ABI Beacon IP21 with Isolator (RED) | 0.65 | 1.55 |  | 0 | 0
VALKYRIE ASBI | Addressable VALKYRIE ASBI Sounder Beacon IP21 with Isolator | 0.65 | 9.05 |  | 0 | 0
VULCAN 2 AS | Addressable Vulcan AS Sounder IP21 (RED) | 0.5 | 7 |  | 0 | 0
VULCAN 2 AB | Addressable Vulcan AB Beacon IP21 (RED) | 0.5 | 2.5 |  | 0 | 0
VULCAN 2 ASB | Addressable Vulcan ASB Sounder Beacon IP21 (RED) | 0.5 | 8 |  | 0 | 0
VOICE SOUNDERS
GFE P.A. VOX -A | Addressable P.A. Speaker Amplifier Dual Gang Box | 0.5 | 0.5 |  | 0 | 0
VALKYRIE VOX - A | VALKYRIE Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VALKYRIE VOX - AB | VALKYRIE Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
VULCAN 2 VOX - A | VULCAN Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VULCAN 2 VOX - AB | VULCAN Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
DOOR HOLDERS
GFE-DHA-ISOLATOR | Addressable Magnetic Door Holder (200N) - ULOW POWER | 0.8 | 7 |  | 0 | 0
LOOP POWERED BEAMS
FIREBEAM BLUE | Firebeam Blue - distance of 7 - 70 meters (Maximum of 6 per Loop) | 24 | 24 |  | 0 | 0
| Loop total devices (excl panels & repeaters) | 0 | LOOP GOOD
| Total quiesent current draw mA (Max 150mA) | 0 | [8 empty] | 1
| Total alarm current draw mA (Max 900mA) | 0 | [8 empty] | 1
| Contact resistance | 0
| Loop total dveices | 0 |  | 0 | 0
Total quiesent current draw
| Total alarm current draw mA | 0 | 0
| Contact reistance | 0.04

## Loop Load Calculator 4
Project:
Loop:
Loop Description:
GREEN CELLS BELOW INDICATE MAXIMUM PERMISSABLE LOOP LENGTH
Part number | Description | Current Draw Quiescent | Current Draw Alarm | Quantity | Current Total Alarm | Current Total Quiesent | Loop Length 1mm multicore | Loop Resistance ohm | Loop Length 1.5mm multicore | Loop Resistance ohm | Char Wire | Char Wire + Conatct | Char Wire | Char Wire + Contact | Detector per section | Current draw AVE | Current per sec | Volt Drop | Volt Drop X 12 | Volt Drop | Volt Drop X 12
PANELS | [6 empty] | 150 | 2.15 | 150 | 1.5176 | 1.77 | 2.15 | 1.3275 | 1.5176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GEKKO | GEKKO Addressable 2.4 Amp PSU | 65 | 65 |  | 0 | 0 | 200 | 2.8667 | 200 | 2.0235 | 2.36 | 2.8667 | 1.77 | 2.0235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON MINI REPEATER -NETWORKED | GEKKO Mini Repeater for Networks | 65 | 65 |  | 0 | 0 | 250 | 3.5833 | 250 | 2.5294 | 2.95 | 3.5833 | 2.2125 | 2.5294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CHAMELEON DISPLAY REPEATER -SINGLE USE | GEKKO Single use Repeater | 65 | 65 |  | 0 | 0 | 300 | 4.3 | 300 | 3.0353 | 3.54 | 4.3 | 2.655 | 3.0353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
OCTO+ - 1 LOOP | OCTO+ Addressable Panel 1 Loop 2.4 Amp PSU | 80 | 80 |  | 0 | 0 | 350 | 5.0167 | 350 | 3.5412 | 4.13 | 5.0167 | 3.0975 | 3.5412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
528-E | NODE PLUS | 80 | 80 |  | 0 | 0 | 400 | 5.7333 | 400 | 4.0471 | 4.72 | 5.7333 | 3.54 | 4.0471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
DETECTORS | [6 empty] | 450 | 6.45 | 450 | 4.5529 | 5.31 | 6.45 | 3.9825 | 4.5529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830 | Addressable Multisensor - EN54 Certified | 0.55 |  |  | 0 | 0 | 500 | 7.1667 | 500 | 5.0588 | 5.9 | 7.1667 | 4.425 | 5.0588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA830CO | Addressable Multisensor with CO & Pre-Alarm function | 0.65 |  |  | 0 | 0 | 550 | 7.8833 | 550 | 5.5647 | 6.49 | 7.8833 | 4.8675 | 5.5647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZA831 | Addressable Multisensor with Sounder Beacon - EN54 Certified | 0.55 | 8.9 |  | 0 | 0 | 600 | 8.6 | 600 | 6.0706 | 7.08 | 8.6 | 5.31 | 6.0706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
REMOTE INDICATORS | [6 empty] | 650 | 9.3167 | 650 | 6.5765 | 7.67 | 9.3167 | 5.7525 | 6.5765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-C | Conventional Minidisc Remote Indicator |  | 2 |  | 0 | 0 | 700 | 10.0333 | 700 | 7.0824 | 8.26 | 10.0333 | 6.195 | 7.0824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-REM-IND-A | Addressable Remote Indicator | 0.3 | 7 |  | 0 | 0 | 750 | 10.75 | 750 | 7.5882 | 8.85 | 10.75 | 6.6375 | 7.5882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LINE MODULES | [6 empty] | 800 | 11.4667 | 800 | 8.0941 | 9.44 | 11.4667 | 7.08 | 8.0941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAM | Addressable Manually Addressed Module | 1.8 | 12 |  | 0 | 0 | 850 | 12.1833 | 850 | 8.6 | 10.03 | 12.1833 | 7.5225 | 8.6 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O | Addressable I/O Module with Isolator & Dual Gang Box | 1.3 | 2.9 |  | 0 | 0 | 900 | 12.9 | 900 | 9.1059 | 10.62 | 12.9 | 7.965 | 9.1059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-AD-ISO | Addressable Stand Alone Loop Isolator | 1 | 1.65 |  | 0 | 0 | 950 | 13.6167 | 950 | 9.6118 | 11.21 | 13.6167 | 8.4075 | 9.6118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
I/O-ISO | Addressable INPUT / OUTPUT Module | 0.5 | 2 |  | 0 | 0 | 1000 | 14.3333 | 1000 | 10.1176 | 11.8 | 14.3333 | 8.85 | 10.1176 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAINS I/O | Addressable Mains Switching INPUT / OUTPUT Module | 1.3 | 2.9 |  | 0 | 0 | 1050 | 15.05 | 1050 | 10.6235 | 12.39 | 15.05 | 9.2925 | 10.6235 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
INPUT | Addressable INPUT MODULE | 0.5 | 2 |  | 0 | 0 | 1100 | 15.7667 | 1100 | 11.1294 | 12.98 | 15.7667 | 9.735 | 11.1294 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
LSCISO | Addressable Opto Isolated Loop Sounder Controller (Ext Power) | 0 | 0 |  | 0 | 0 | 1150 | 16.4833 | 1150 | 11.6353 | 13.57 | 16.4833 | 10.1775 | 11.6353 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ZMU | Addressable Zone Monitoring Unit | 1.8 | 25 |  | 0 | 0 | 1200 | 17.2 | 1200 | 12.1412 | 14.16 | 17.2 | 10.62 | 12.1412 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
QUAD ZMU | Addressable Conventional Zone Monitoring Unit | 1.8 |  |  | 0 | 0 | 1250 | 17.9167 | 1250 | 12.6471 | 14.75 | 17.9167 | 11.0625 | 12.6471 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4 INPUT | Addressable 4 Input | 2.6 |  |  | 0 | 0 | 1300 | 18.6333 | 1300 | 13.1529 | 15.34 | 18.6333 | 11.505 | 13.1529 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
8 INPUT | Addressable 8 Input | 3.2 |  |  | 0 | 0 | 1350 | 19.35 | 1350 | 13.6588 | 15.93 | 19.35 | 11.9475 | 13.6588 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CCPI 8 ZONES | Addressable Conventional Control Panel Interface Up To 8 Zones | 3.2 |  |  | 0 | 0 | 1400 | 20.0667 | 1400 | 14.1647 | 16.52 | 20.0667 | 12.39 | 14.1647 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
SPRINKLER SWITCH | Addressable Sprinkler Switch Module | 0.55 |  |  | 0 | 0 | 1450 | 20.7833 | 1450 | 14.6706 | 17.11 | 20.7833 | 12.8325 | 14.6706 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CALL POINTS | [6 empty] | 1500 | 21.5 | 1500 | 15.1765 | 17.7 | 21.5 | 13.275 | 15.1765 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-A | Addressable Call Point Red Resettable IP24 | 0.45 |  |  | 0 | 0 | 1550 | 22.2167 | 1550 | 15.6824 | 18.29 | 22.2167 | 13.7175 | 15.6824 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
GFE-MCPE-AI | Addressable Call Point Red Resettable IP24 with Loop Isolator | 0.65 |  |  | 0 | 0 | 1600 | 22.9333 | 1600 | 16.1882 | 18.88 | 22.9333 | 14.16 | 16.1882 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
STANDALONE SOUNDER/BEACONS | [6 empty] | 1650 | 23.65 | 1650 | 16.6941 | 19.47 | 23.65 | 14.6025 | 16.6941 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AS | Addressable VALKYRIE AS Sounder IP21 (RED) | 0.5 | 7.5 |  | 0 | 0 | 1700 | 24.3667 | 1700 | 17.2 | 20.06 | 24.3667 | 15.045 | 17.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE AB | Addressable VALKYRIE AB Beacon IP21 (RED) | 0.5 | 1.4 |  | 0 | 0 | 1750 | 25.0833 | 1750 | 17.7059 | 20.65 | 25.0833 | 15.4875 | 17.7059 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASB | Addressable VALKYRIE ASB Sounder Beacon IP21 (RED) | 0.5 | 8.9 |  | 0 | 0 | 1800 | 25.8 | 1800 | 18.2118 | 21.24 | 25.8 | 15.93 | 18.2118 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
VALKYRIE ASI | Addressable VALKYRIE ASI Sounder IP21 with Isolator (RED) | 0.65 | 7.65 |  | 0 | 0
VALKYRIE ABI | Addressable VALKYRIE ABI Beacon IP21 with Isolator (RED) | 0.65 | 1.55 |  | 0 | 0
VALKYRIE ASBI | Addressable VALKYRIE ASBI Sounder Beacon IP21 with Isolator | 0.65 | 9.05 |  | 0 | 0
VULCAN 2 AS | Addressable Vulcan AS Sounder IP21 (RED) | 0.5 | 7 |  | 0 | 0
VULCAN 2 AB | Addressable Vulcan AB Beacon IP21 (RED) | 0.5 | 2.5 |  | 0 | 0
VULCAN 2 ASB | Addressable Vulcan ASB Sounder Beacon IP21 (RED) | 0.5 | 8 |  | 0 | 0
VOICE SOUNDERS
GFE P.A. VOX -A | Addressable P.A. Speaker Amplifier Dual Gang Box | 0.5 | 0.5 |  | 0 | 0
VALKYRIE VOX - A | VALKYRIE Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VALKYRIE VOX - AB | VALKYRIE Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
VULCAN 2 VOX - A | VULCAN Addressable Voice Sounder IP21 (RED) | 0.7 | 7.5 |  | 0 | 0
VULCAN 2 VOX - AB | VULCAN Addressable Voice Sounder Beacon IP21 (RED) | 0.7 | 8.9 |  | 0 | 0
DOOR HOLDERS
GFE-DHA-ISOLATOR | Addressable Magnetic Door Holder (200N) - ULOW POWER | 0.8 | 7 |  | 0 | 0
LOOP POWERED BEAMS
FIREBEAM BLUE | Firebeam Blue - distance of 7 - 70 meters (Maximum of 6 per Loop) | 24 | 24 |  | 0 | 0
| Loop total devices (excl panels & repeaters) | 0 | LOOP GOOD
| Total quiesent current draw mA (Max 150mA) | 0 | [8 empty] | 1
| Total alarm current draw mA (Max 900mA) | 0 | [8 empty] | 1
| Contact resistance | 0
| Loop total dveices | 0 |  | 0 | 0
Total quiesent current draw
| Total alarm current draw mA | 0 | 0
| Contact reistance | 0.04